## Slide 1
MEAM 5020 Final Project
Rack Manifold Optimization
Constantin de Lint, David Kim, Jason Simon, Sam Vasington
Assignment 4: Previous work, design changes, and calculation plan
Notes: Template supplied by the user: MEAM 5020 Final Project (1).pdf. The supplied group names are retained. The PDF design is rebuilt as editable slide elements, with original brand assets. This is an NVL72-inspired design study, not a validated NVIDIA product design.

## Slide 2
Coolant Distribution Across an AI Rack
2
[4] [7] Sources and calculation details in speaker notes.
Compute
Switch
Compute
Supply
Return
Purpose
Deliver the cooling flow each tray needs while limiting pressure loss and pump power.
How it works
A supply header feeds parallel tray branches. Cold plates absorb heat; a return header carries it to the CDU heat exchanger.
18 compute trays + 9 switch trays
72 GPUs + 36 CPUs
Different heat loads and flow resistances create different cooling needs.
Notes: [4] NVIDIA. DGX GB Rack Scale Systems User Guide, Hardware. https://docs.nvidia.com/dgx/dgxgb200-user-guide/hardware.html
[7] Local project source and recalculated results, 15 September 2026. config/baseline.yaml, config/optimized_example.yaml, src/nvl72/{solver,hydraulics,thermal,orifices,cdu,facility,objectives}.py. Repository: https://github.com/jasonsimon999/NVL72-Manifold-Optimization

## Slide 3
Three Approaches From Previous Work
3
[1] [2] [3] Sources and calculation details in speaker notes.
Previous approach | Evidence | Use in this project
[1] Patterned branch orifices Sogunuru et al., 2020 | Electronics cooling with unequal flow targets | Selected baseline: tune branch resistance to heat load
[2] Tapered header Hassan et al., 2014 | At Re = 150,000, reported Φ falls from 0.0345 to 0.0140 | Compare header taper against added restrictions
[3] Header shape and inlet Anbumeenakshi & Thansekhar, 2016 | 25 water microchannels; best shape depends on flow rate | Test operating range before selecting geometry
Notes: The three core references are original research. Study [1] is the selected baseline method. Reported nonuniformity in [2] is its own metric, not the project RMS metric.
[1] Sogunuru A, Menon YK, Niranjanappa AC, Reddy KH. Numerical and Experimental Investigations on Patterned Flow Distribution through Manifolds in Electronics Cooling. IJMPERD. 2020;10(2):975–986. https://scispace.com/pdf/numerical-and-experimental-investigations-of-patterned-flow-6skn0d5dfr.pdf
[2] Hassan JM, Mohamed TA, Mohammed WS, Alawee WH. Modeling the Uniformity of Manifold with Various Configurations. Journal of Fluids. 2014;325259. https://doi.org/10.1155/2014/325259
[3] Anbumeenakshi C, Thansekhar MR. Experimental investigation of header shape and inlet configuration on flow maldistribution in microchannel. Experimental Thermal and Fluid Science. 2016;75:156–161. https://doi.org/10.1016/j.expthermflusci.2016.02.004

## Slide 4
Selected Baseline: Patterned Orifice Sizing
4
[1] [7] Sources and calculation details in speaker notes.
Published setup [1] | Value
Configuration | Z-type, water, 1 L/min total
Header / branch ID | 12 mm / 6.5 mm
Channels / length | 10 channels / 700 mm
Pattern 1 example | 2.1–2.4 mm bores in branches 1, 3, 5, 7, 9
Why this baseline?
It directly links unequal electronics heat loads to individually sized restrictions.
Our extension
Couple 27 tray branches to temperature-dependent properties, component losses, and CDU limits.
Rack geometry is assumed; reproducing the literature benchmark is a future validation step.
Notes: Reference [1], sections 3–6 and Table 1. Its narrative and Table 2 disagree on experimental deviation, so no accuracy percentage is adopted. The paper benchmark has not yet been reproduced by our code.
[1] Sogunuru A, Menon YK, Niranjanappa AC, Reddy KH. Numerical and Experimental Investigations on Patterned Flow Distribution through Manifolds in Electronics Cooling. IJMPERD. 2020;10(2):975–986. https://scispace.com/pdf/numerical-and-experimental-investigations-of-patterned-flow-6skn0d5dfr.pdf
[7] Local project source and recalculated results, 15 September 2026. config/baseline.yaml, config/optimized_example.yaml, src/nvl72/{solver,hydraulics,thermal,orifices,cdu,facility,objectives}.py. Repository: https://github.com/jasonsimon999/NVL72-Manifold-Optimization

## Slide 5
Physical Changes to the Manifold
5
[1] [7] Sources and calculation details in speaker notes.
Compute
Switch
Compute
Supply
Return
Replaceable orifice inserts
Set compute and switch bores separately; allow a different bore at each tray.
Header diameter and taper
Adjust the main passage to manage pressure variation along the rack.
Branch and QD passage sizes
Vary flow area; verify with measured loss curves.
Schematic, not to scale
Notes: Conceptual editable diagram, not a dimensioned NVIDIA drawing. Red circles identify added replaceable orifice inserts. Header sizing/taper and quick disconnect bore are additional design variables. Three representative branches stand for 27.
[1] Sogunuru A, Menon YK, Niranjanappa AC, Reddy KH. Numerical and Experimental Investigations on Patterned Flow Distribution through Manifolds in Electronics Cooling. IJMPERD. 2020;10(2):975–986. https://scispace.com/pdf/numerical-and-experimental-investigations-of-patterned-flow-6skn0d5dfr.pdf
[7] Local project source and recalculated results, 15 September 2026. config/baseline.yaml, config/optimized_example.yaml, src/nvl72/{solver,hydraulics,thermal,orifices,cdu,facility,objectives}.py. Repository: https://github.com/jasonsimon999/NVL72-Manifold-Optimization

## Slide 6
Goal and Design
6
[7] Sources and calculation details in speaker notes.
Project item | Definition
Problem / project type | Unequal cooling allocation / component design
Primary goal | Match each tray flow to its heat load
Proposed target | RMS flow-target error ≤ 5% at the design point
Design variables | Header ID/taper; compute, switch, and per-tray bores
Secondary objectives | Minimize outlet temperature, pump power, and header volume
Study constraints | Outlet ≤ 65 °C; header velocity ≤ 3 m/s; 0 < bore < branch ID
Decision rule | Check fixed hardware and pump capability off-design
Notes: Targets shown here are proposed study criteria, not measured product specifications. Compare candidates at matched coolant, total rack flow, inlet temperature, and heat load. A flow error metric must use heat-proportional targets rather than equal flow.
[7] Local project source and recalculated results, 15 September 2026. config/baseline.yaml, config/optimized_example.yaml, src/nvl72/{solver,hydraulics,thermal,orifices,cdu,facility,objectives}.py. Repository: https://github.com/jasonsimon999/NVL72-Manifold-Optimization

## Slide 7
Rack Calculation Inputs and Assumptions
7
[4] [7] Sources and calculation details in speaker notes.
Input | Study value | Evidence status
Rack topology | 18 compute + 9 switch trays | Published topology [4]
Liquid heat scenario | 18 × 5.80 + 9 × 1.24 = 115.56 kW | Model load assumptions
Rack coolant / supply / flow | Legacy PG25 / 40 °C / 120 L/min | Chosen operating point
Headers / branch IDs | 38 mm / compute 8 mm, switch 6 mm | Assumed internal diameters
QD and cold-plate losses | Separate reduced resistance coefficients | Estimated, not measured curves
Facility water | 36 °C, 150 L/min, one rack | Scenario, not a facility limit
Notes: These inputs reproduce config/baseline.yaml and config/optimized_example.yaml. Electrical component power is treated as heat entering coolant in this scenario. Actual liquid heat capture and switch load need measurements. Legacy PG25 is retained to reproduce the earlier study, not endorsed over manufacturer properties.
[4] NVIDIA. DGX GB Rack Scale Systems User Guide, Hardware. https://docs.nvidia.com/dgx/dgxgb200-user-guide/hardware.html
[7] Local project source and recalculated results, 15 September 2026. config/baseline.yaml, config/optimized_example.yaml, src/nvl72/{solver,hydraulics,thermal,orifices,cdu,facility,objectives}.py. Repository: https://github.com/jasonsimon999/NVL72-Manifold-Optimization

## Slide 8
Mass Balance and Heat-Proportional Flow
8
[7] Sources and calculation details in speaker notes.
1. Conserve coolant at every junction
Σ ṁin = Σ ṁout and Σ ṁi = ṁrack
2. Allocate flow according to heat
ṁi* = ṁrack × Q̇i / Σ Q̇i
At 120 L/min: compute target = 6.02 L/min per tray; switch = 1.29 L/min.
3. Solve each tray energy balance
Q̇i = ṁi [h(Tout,i) − h(Tin)] h(T) = ∫ cp(T) dT
Flow error (%) = 100 √{(1/n) Σ [(ṁi / ṁi*) − 1]²}
Notes: Notation: ṁ = mass flow (kg/s), Q̇ = thermal power (W), V̇ = volume flow (m³/s), h = specific enthalpy (J/kg), cp = specific heat (J/kg/K). Common inlet state makes inlet-reference volume targets proportional to heat. Exact thermal calculation integrates the tabulated cp(T).
[7] Local project source and recalculated results, 15 September 2026. config/baseline.yaml, config/optimized_example.yaml, src/nvl72/{solver,hydraulics,thermal,orifices,cdu,facility,objectives}.py. Repository: https://github.com/jasonsimon999/NVL72-Manifold-Optimization

## Slide 9
Pressure Loss and Orifice Sizing
9
[7] Sources and calculation details in speaker notes.
Pipe and fitting losses
Δp = (f L/D + ΣK) ρv²/2
Re = ρvD/μ
Use 64/Re in laminar flow; a Haaland relation in turbulent flow, with a transition blend.
Network closure
Each complete supply–tray–return path has the same end-to-end pressure difference. Include elevation head.
Permanent orifice loss
Δporifice = Kh ṁ²
β = d/D Ao = πd²/4
Kh = [√(1 − β⁴(1 − Cd²)) − Cd β²]²
/ (2ρ Cd² Ao²)
For required Kh, invert this relation to obtain bore d. Smaller bores increase resistance.
0 < d < D; Cd = 0.62 is assumed.
Notes: Equations implemented in components.py and orifices.py. Kh has units Pa/(kg/s)^2 and differs from dimensionless minor-loss K. Cd = 0.62 is a screening assumption for a thin, sharp-edged plate. The permanent-loss relation accounts for recovery; pressure-tap differential alone is not permanent loss. Header model omits 3D tee momentum recovery.
[7] Local project source and recalculated results, 15 September 2026. config/baseline.yaml, config/optimized_example.yaml, src/nvl72/{solver,hydraulics,thermal,orifices,cdu,facility,objectives}.py. Repository: https://github.com/jasonsimon999/NVL72-Manifold-Optimization

## Slide 10
Pump and Facility Heat-Exchanger Balance
10
[7] Sources and calculation details in speaker notes.
Pump operating point and electrical power
Δppump = Δp0 N² − aV̇² = Δpsystem Pe = Δp V̇ / η
Fixed-flow mode evaluates the head required. Pump mode solves the curve intersection.
Facility water removes the rack heat
Q̇HX = Σ Q̇i = ṁFWS [h(TFWS,out) − h(TFWS,in)]
Heat-exchanger conductance required
UArequired = Q̇HX / ΔTlm ΔTlm = (ΔT1 − ΔT2) / ln(ΔT1/ΔT2)
Notes: Pump curve uses an assumed parabolic shape fitted to a nominal point and assumed shutoff head. It is not a measured manufacturer curve. Pinches: ΔT1 = rack return minus facility return; ΔT2 = rack supply minus facility supply. Both must be positive. Equal terminal differences use the continuous LMTD limit. No ambient heat loss or pump heat is included in the quoted rack balance.
[7] Local project source and recalculated results, 15 September 2026. config/baseline.yaml, config/optimized_example.yaml, src/nvl72/{solver,hydraulics,thermal,orifices,cdu,facility,objectives}.py. Repository: https://github.com/jasonsimon999/NVL72-Manifold-Optimization

## Slide 11
Flow Redistribution Matches Cooling Demand
11
[7] Sources and calculation details in speaker notes.
Chart: Flow per tray (L/min)
| Compute tray | Switch tray
Target | 6.02 | 1.29
Reference | 5.21 | 2.91
Balanced | 6.02 | 1.29
Same total flow
Restricting over-supplied switch branches redirects coolant to compute trays.
Equal flow is not the objective: the modeled compute heat load is 4.68× larger.
Notes: Fresh solve on 15 September 2026. Chart values are the arithmetic mean per tray class, in inlet-reference L/min. This is a comparison at the same total 120 L/min. The class means hide within-class variation, so the next slide includes a 27-tray RMS metric.
[7] Local project source and recalculated results, 15 September 2026. config/baseline.yaml, config/optimized_example.yaml, src/nvl72/{solver,hydraulics,thermal,orifices,cdu,facility,objectives}.py. Repository: https://github.com/jasonsimon999/NVL72-Manifold-Optimization

## Slide 12
Better Distribution Requires More Pumping
12
[7] Sources and calculation details in speaker notes.
Metric | Reference | Balanced
RMS flow-target error | 73.49% | 0.44%
Maximum tray outlet | 55.97 °C | 53.80 °C
Tray outlet temperature spread | 9.90 K | 0.21 K
Required system pressure | 79.83 kPa | 105.09 kPa
Modeled pump electrical power | 266.1 W | 350.3 W
Mixed rack return temperature | 53.73 °C | 53.73 °C
Maximum outlet falls 2.17 K; pumping rises 84.2 W (+31.6%).
Heat and total flow are unchanged, so the mixed return stays the same.
Notes: Recalculated from baseline.yaml and optimized_example.yaml. Balanced design retains 38 mm constant headers, compute added Kh = 0 and switch added Kh = 180528785.8784 Pa/(kg/s)^2. Pump efficiency is 0.60. Results are modeled, not hardware measurements or a proven global optimum. Legacy PG25 properties and fixed component resistance coefficients reproduce the earlier study.
[7] Local project source and recalculated results, 15 September 2026. config/baseline.yaml, config/optimized_example.yaml, src/nvl72/{solver,hydraulics,thermal,orifices,cdu,facility,objectives}.py. Repository: https://github.com/jasonsimon999/NVL72-Manifold-Optimization

## Slide 13
Existing Code and Data to Reuse
13
[5] [6] [7] Sources and calculation details in speaker notes.
Resource | Role | Status
SciPy least_squares [6] | Solve nonlinear hydraulic residuals with bounds | Already used
Project Python model [7] | Network, coolant properties, sweeps, constraints, Streamlit | Already implemented
CoolProp INCOMP database [5] | Independent water/glycol property check | Proposed cross-check
Calculation workflow
Solve flows and temperatures, update properties, and iterate.
Then check constraints and compare designs.
Notes: Existing code requirement: the repository already calls SciPy least_squares for hydraulic closure; it is not a solver written from scratch. CoolProp is a proposed independent property cross-check and is not the current runtime property engine. Its fluid-specific composition convention must be respected.
[5] CoolProp. Incompressible Fluids documentation. https://coolprop.org/fluid_properties/Incompressibles.html
[6] SciPy. scipy.optimize.least_squares documentation. https://docs.scipy.org/doc/scipy/reference/generated/scipy.optimize.least_squares.html
[7] Local project source and recalculated results, 15 September 2026. config/baseline.yaml, config/optimized_example.yaml, src/nvl72/{solver,hydraulics,thermal,orifices,cdu,facility,objectives}.py. Repository: https://github.com/jasonsimon999/NVL72-Manifold-Optimization

## Slide 14
Checks Needed Before Choosing Hardware
14
[7] Sources and calculation details in speaker notes.
Numerical checks passed
Both example cases converge and satisfy mass, energy, and pressure closure.
Validate the inputs that drive the answer
Measure tray/QD pressure–flow curves and orifice discharge behavior. Obtain chip limits, thermal resistance, and facility/CDU performance maps.
Test fixed hardware across operating conditions
Sweep flow, workload split, coolant, and inlet temperature. Include bore tolerances, partial blockage, and reduced pump capability.
The 1D model omits 3D tee momentum recovery. Verify header-shape benefits with CFD.
Notes: Recalculated numerical closure for both cases: mass relative error ≤ 2.18e-16; energy relative error ≤ 2.40e-15; pressure residual ≤ 4.37e-11 Pa. These show numerical closure only. Review properties, chip thermal resistance, QD curves, and actual pump/HX maps. Do not treat the 80 °C assumed target as an NVIDIA throttling threshold.
[7] Local project source and recalculated results, 15 September 2026. config/baseline.yaml, config/optimized_example.yaml, src/nvl72/{solver,hydraulics,thermal,orifices,cdu,facility,objectives}.py. Repository: https://github.com/jasonsimon999/NVL72-Manifold-Optimization

## Slide 15
References and Calculation Record
15
[1] Sogunuru et al. (2020). Patterned flow distribution through manifolds in electronics cooling. IJMPERD 10(2), 975–986. Selected calculation baseline.
[2] Hassan et al. (2014). Modeling the Uniformity of Manifold with Various Configurations. Journal of Fluids. doi:10.1155/2014/325259.
[3] Anbumeenakshi & Thansekhar (2016). Header shape and inlet configuration in microchannels. Experimental Thermal and Fluid Science 75, 156–161. doi:10.1016/j.expthermflusci.2016.02.004.
[4] NVIDIA DGX GB Rack Scale Systems User Guide: Hardware.
[5] CoolProp: Incompressible Fluids database and documentation.
[6] SciPy: scipy.optimize.least_squares documentation.
[7] NVL72-Manifold-Optimization repository. Matched reference and balanced runs recalculated on 15 September 2026. Full source links and details are in slide notes.
Notes: [1] Sogunuru A, Menon YK, Niranjanappa AC, Reddy KH. Numerical and Experimental Investigations on Patterned Flow Distribution through Manifolds in Electronics Cooling. IJMPERD. 2020;10(2):975–986. https://scispace.com/pdf/numerical-and-experimental-investigations-of-patterned-flow-6skn0d5dfr.pdf
[2] Hassan JM, Mohamed TA, Mohammed WS, Alawee WH. Modeling the Uniformity of Manifold with Various Configurations. Journal of Fluids. 2014;325259. https://doi.org/10.1155/2014/325259
[3] Anbumeenakshi C, Thansekhar MR. Experimental investigation of header shape and inlet configuration on flow maldistribution in microchannel. Experimental Thermal and Fluid Science. 2016;75:156–161. https://doi.org/10.1016/j.expthermflusci.2016.02.004
[4] NVIDIA. DGX GB Rack Scale Systems User Guide, Hardware. https://docs.nvidia.com/dgx/dgxgb200-user-guide/hardware.html
[5] CoolProp. Incompressible Fluids documentation. https://coolprop.org/fluid_properties/Incompressibles.html
[6] SciPy. scipy.optimize.least_squares documentation. https://docs.scipy.org/doc/scipy/reference/generated/scipy.optimize.least_squares.html
[7] Local project source and recalculated results, 15 September 2026. config/baseline.yaml, config/optimized_example.yaml, src/nvl72/{solver,hydraulics,thermal,orifices,cdu,facility,objectives}.py. Repository: https://github.com/jasonsimon999/NVL72-Manifold-Optimization
Assignment coverage: three previous works (3), selected baseline (4), physical changes with circles/arrows (5), governing equations (8–10), existing code/database (13). No contribution hours are invented.